|  |
| --- |
| **Engineering Conditions of Acceptability** |
| For use only in or with complete equipment where the acceptability of the combination is determined by UL LLC. When installed in an end-product, consideration must be given to the following: |
| 1. The following Production-Line tests are conducted for this product: Electric Strength |
| 1. The following secondary output circuits are SELV: All |
| 1. The power supply terminals and/or connectors are: Suitable for field wiring |
| 1. The maximum investigated branch circuit rating is: 20 A |
| 1. The investigated Pollution Degree is: 2 |
| 1. The following magnetic devices (e.g. transformers or inductor) are provided with an OBJY2 insulation system with the indicated rating greater than Class A (105°C): L3 - Class 130 (B) (see appended table 1.5.1) |
| 1. The following end-product enclosures are required: Fire , Electrical |
| 1. The following secondary output circuits are at non-hazardous energy levels: All |
| 1. The end-product Electric Strength Test is to be based upon a maximum working voltage of: Primary-SELV: 256 Vrms, 614 Vpk |