|  |
| --- |
| **Engineering Conditions of Acceptability**  |
| For use only in or with complete equipment where the acceptability of the combination is determined by UL LLC. When installed in an end-product, consideration must be given to the following:  |
| 1. The following Production-Line tests are conducted for this product: Electric Strength
 |
| 1. The end-product Electric Strength Test is to be based upon a maximum working voltage of: Primary-SELV: , PEL230/18-2.5: 289.2 Vrms, 630 Vpk, PEL230/5-5.5: 295.2 Vrms, 655 Vpk
 |
| 1. The following secondary output circuits are SELV: All
 |
| 1. The following secondary output circuits are at non-hazardous energy levels: All
 |
| 1. The power supply terminals and/or connectors are: Suitable for field wiring
 |
| 1. The maximum investigated branch circuit rating is: 20 A
 |
| 1. The investigated Pollution Degree is: 2
 |
| 1. The following magnetic devices (e.g. transformers or inductor) are provided with an OBJY2 insulation system with the indicated rating greater than Class A (105°C): L3 (Class F); L2 (Class B)
 |
| 1. The following end-product enclosures are required: Fire, Electrical
 |